## Slide 1: Neutral blocking of Transformer GMD/GIC: why a Surge Arrester
Alberto Ramirez Orquin Vanessa Ramirez
Resilient Grids, LLC
Audio Presentation

## Slide 2: General
Introducing a simple, cost-effective means to deal with this major hazard by means of an innovative surge-arrester GIC-blocking principle
Essential discussion regarding the impact upon transformer grounding of devices based on neutral GIC blocking

## Slide 3
Key application to a typical Autotransformer
Significant invariance of the grounding ratios after a proposed arrester device deployment
Important revealed features set plausible benchmarking with alternative capacitive blocking devices
General

## Slide 4: The Surge Arrester Protective Functionality
In addition to transformer and line protection surge arresters/(MOV) have been extensively utilized for series- capacitor protection
Transformer neutral-blocking devices use surge arresters for overvoltage protection

## Slide 5: The Surge-Arrester Protective Functionality: its application to neutral-blocking devices
Exhaustive testing series performed at major high-power Labs
Full-scale testing series performed at major high-voltage Labs
Comprehensive simulations at both academic and industrial levels
.

## Slide 6: The Surge Arrester Dual Functionality
Ohm’s Law applies to non-linear resistors; mind
slopes at graph points of both Regions I and II

## Slide 7: The Surge Arrester Dual Functionality
Region I: Resistance very high; consistent with GMD voltages
Region II: Resistance very low; consistent with ground-fault disturbances

## Slide 8
Comparative of Transformer Neutral Voltage Ranges

## Slide 9: Why a Neutral-Blocking Capacitor?

## Slide 10: Why a Neutral-Blocking Capacitor?
Industry reluctance to this approach is due to costs, size, complexity and perceived operational risks *
Understanding this problem, and its solution, starts with consideration of three power-system design states
* Failure modes for the most part unknown

## Slide 11: Neutral-Blocking Capacitor Facts
Neutral surge arrester protects the shunt capacitor bank from ground faults
Surge arrester also protects all components connected neutral-to-ground, including the winding neutral insulation to ground (typically 110 KV BIL)

## Slide 12: Neutral-Blocking Capacitor Facts
At ground faults surge arrester instantaneously by-passes the capacitor bank thus protecting the transformer wye winding by solidly grounding its neutral
Any perceived neutral-grounding capacitor function hence rendered unnecessary

## Slide 13: Neutral-Blocking Capacitor Facts
Through a ground fault, surge arrester does fully protect transformer winding neutral-end, besides solidly grounding it after a few milliseconds from fault inception; with or without a shunt capacitor
Significant electric utility practice on grid transformer ungrounded wye design, with neutral surge arrester applications, feasible even in that substantially more demanding steady-state operation

## Slide 14: Basic Power-system device design states
Three basic power-system device design states to consider, possibly in combination:
  a) Ground-Fault Disturbances
  b) GMD/GIC
  c) Steady State

## Slide 15: Simultaneous Condition
Ground Fault and GMD/GIC
Mitigation Device Deployed
Inconsequential; transformer protected by Surge Arrester

## Slide 16: GIC-State Condition
Steady State and GMD/GIC
Mitigation Device Not Deployed
Problematic; transformer traversed by GIC currents

## Slide 17: Why a Neutral-Blocking Capacitor
GMD/GIC Disturbance
Mitigation Device Deployed
Inconsequential; transformer protected by a neutral-blocking scheme

## Slide 18: Why a GIC Neutral-Blocking Surge Arrester
GMD/GIC Disturbance
Surge arrester, in parallel with capacitor, performs a not duly appreciated blocking function identical to the one carried out
by the capacitor
Otherwise GIC current could flow
to ground through surge-arrester
path
Actually, there is a record of that problem happening in a well-documented case

## Slide 19
Capacitor Scheme Alternatives
Capacitor Neutral-Blocking Device
Alternative Capacitor Device

## Slide 20
Critical Considerations
Capacitor-bank footprint/rating, a limiting factor
Capacitor-bank constrained to Distribution lower-voltage ratings
Protective devices consequently constrained to Distribution lower-voltage ratings

## Slide 21
Critical Considerations
As protective devices are constrained to Distribution lower-voltage ratings a sizable EMP impact will set a neutral voltage causing either a surge arrester bypass to ground or alternatively conduction of the spark gap
GIC will then flow through the transformer to ground

## Slide 22: Higher blocking-device ratings and attendant protecting devices (say up to 20 KV) could be attempted, despite its exponential cost/size impact, to prevent EMP shocks from circumventing the unit However, ground faults causing lower than said 20 KV neutral voltages would directly impact both device capacitor and resonance-damping resistors setting extreme power-rating requirements for a critical time until protective switching happens
The Capacitor Neutral-Blocking Device Dilemma

## Slide 23
Critical Considerations
The only constraint upon a single Surge-arrester device stems from its dual-functionality requirements
Much higher ratings possible making EMP neutral voltage inductions inconsequential to GIC blocking

## Slide 24: Why a GIC Neutral-blocking Surge Arrester
We Propose

## Slide 25: Why a GIC Neutral-blocking Surge Arrester
It must therefore be concluded, based on state-design criteria, the inclusion of a capacitor bank in a neutral- blocking scheme can not be justified from an engineering standpoint

## Slide 26
Steady-state conditions with proposed arrester-device deployed
Unlikely state for Solar GMD
Very unlikely state for EMP/E3
Why a Neutral-Blocking Surge
Arrester

## Slide 27: Steady-state conditions: Arrester-device deployment Analysis
Impact on all AC steady-state variables
Impact on grounding ratio X0/X1
Impact on zero-sequence current flow
Surge-arrester specs

## Slide 28: Steady-state conditions: Arrester-device deployment Analysis
.
Typical Transformer apparatus:
Three-winding grounded Wye-Wye-Delta Autotransformer
Two-winding Delta-Wye (grounded) GSU

## Slide 29: Normal Steady-State Conditions
Typical three-winding Autotransformer
Positive/negative sequence per-unit equivalent circuit
Zero-sequence per-unit equivalent circuit

## Slide 30: Steady-State Performance
Three-winding Autotransformer/Numerical Example
Grounding Coefficient before and after arrester deployment
Nameplate 500/435/100 MVA 500/345/66 KV
Grounded YY∆ Connection
XHL = 0.10 pu on a 500 KV/500 MVA base
XHT = 0.17 pu on a 500 KV/100 MVA base
XLT = 0.15 pu on a 66 KV/100 MVA base

## Slide 31: Normal Steady-State conditions: Neutral Device deployed
Three-winding Autotransformer
One-line diagram of device-caused neutral-to-ground isolation: zero-
sequence flow
Zero-sequence circuit with neutral isolated from ground

## Slide 32: Steady-State Performance
Three-winding Autotransformer/Numerical Example
Grounding Coefficient before and after neutral arrester deployment
Conversion to 500 MVA base
XHL = 0.10 pu
XHT = 0.17 x 5 = 0.85 pu
XLT = 0.15 x 5 = 0.75 pu

## Slide 33: Steady-State Performance
Three-winding Autotransformer/Numerical Example
Grounding Coefficient for normal conditions
(no arrester blocking device deployment)

## Slide 34: Steady-State Performance
Three-winding Autotransformer
Numerical Example
Grounding Coefficient before and after arrester deployment
Windings reactance computation
XH = 0.5(XHL + XHT - XLT) = 0.5(0.10 + 0.85 - 0.75) = 0.1 pu
XL = 0.5(XHL + XLT - XHT) = 0.5(0.10 + 0.75 - 0.85) = 0.0 pu
XT = 0.5(XLT + XHT - XHL) = 0.5(0.75 + 0.85 - 0.10) = 0.75 pu

## Slide 35
Steady-State Performance
High-to-Tertiary Turns-ratios / Correction factor before and after arrester deployment (causing zero-sequence neutral-to-ground isolation)

## Slide 36: Steady-State Performance
Grounding Coefficient after device deployment
Turns-ratio correction factor
Prevailing zero-sequence High-to-Low reactance becoming:
X’HT = XHT = 0.85 x 0.1 = 0.085 pu

## Slide 37: Steady-State Performance
Three-winding Autotransformer/Numerical Example
Grounding Coefficient after neutral arrester
Deployment

## Slide 38: Steady-State Performance
Three-winding Autotransformer:
Grounding Coefficient Summary
  No neutral arrester deployment = 1.0
  Neutral arrester deployment = 0.85
Note: grounding coefficient of 1.0 corresponds to a solidly-grounded equipment (IEEE Standard)

## Slide 39
It can be then securely asserted, from the steady-state consideration, a capacitor-bank application could not be justified from an engineering standpoint for the protection of a grid autotransformer
Steady-State Performance

## Slide 40: Steady-state Performance GSU Transformer
No zero-sequence flow may come from the generation side
Zero-sequence unbalance flow may develop from the transmission line side due to load or from line-parameter dissymmetry

## Slide 41: Steady-state Performance GSU Transformer
Zero-sequence components typically negligible
Neutral shift would be limited to a Ferranti-rise in the zero-sequence network
Zero-sequence flow through GSU immaterial as it refers to a line-end apparatus
Arrester device lends itself to a straight-forward specification from the unbalance examination

## Slide 42: Conclusions
Steady-state performance, parametrical invariance, GIC blocking, ground-faults, zero-sequence current residuals, etc, the standalone surge-arrester device compares favorably with the one based on a capacitor bank, yet without any of its undeniable inherent risks
The difference can only be found at the blocking-function means: one performed by a capacitor bank and another by a common surge arrester

## Slide 43: Conclusions
Capacitor Device Arrester Device

## Slide 44: Final Thoughts
Legitimate reservations regarding the incremental cost/benefit of adding massive capacitor-bank assemblies, with convoluted ancillaries, merely to secure the flow of inconsequential, quasi-parasitic, ground currents associated to a few transformers at limited and short steady-state situations
Legitimate questions regarding such an incremental cost/benefit evaluation minding neutral-blocking units might operate infrequently and able to reduce basically around fifty percent of GIC upon some autotransformers *
* GIC suppression achievable only by placing one device at each apparatus

## Slide 45: Final Thoughts
Comprehensive utility-industry R&D has established consensus regarding GIC-blocking strategies
Studies on major power grids conclusively indicate that a discrete placing of blockers at selected apparatus will produce only a marginal protective benefit. This becomes critical under EMP conditions
Only way to eliminate GIC from the electricity grid is by the installation of one device at each transformer

## Slide 46: Future/Ongoing Work
R&D on actionable early sensing of EMP shock waves (presently in advanced testing state)
R&D to favorably address the challenging issue of GIC current interruption

## Slide 47: Questions ?
Feel free to contact us and/or also to request a personal presentation of this material for an in-depth discussion
www.resilientgrids.com